## Slide 1
Thierry Pollet
Energy sector executive
Huawei
Panel: Technological developments and equipment costs in photovoltaics, wind, and storage
Athens, November 1st, 2024.

## Slide 2
1st November 2024, Athens
Technological developments in battery storage: Grid Forming (GFM)
(enabling PV integration, Grid stability, Merchant market grid services)

## Slide 3
Thierry Pollet
Energy Sector Executive | Innovator | Power Digitalization
Results-driven transformation leader with 20+ years of experience in innovation management, product management and R&D management for ICT and energy industry.
Successfully developed delivered new products and services to leading companies such as Nokia, Toshiba (L+G), ABB.
Digital transformation lead Hitachi Energy systems BU
Leading role in internal and external startups capitalizing on emerging market opportunities.
Leading world’s first products in high speed internet (xDSL), distribution network state estimation (PMU), digital twins of power stations

## Slide 4
Greek Electricity System
1.
Challenges for large scale RES integration
2.
Grid Stability
3.
New merchant market services (FFR, Inertia)
4.
Grid Forming through battery storage systems
5.
Regulation and standards
6.
Summary & conclusion
7.

## Slide 5: Greek Electricity System
34% Natural gas
23% Wind
17% PV
48TWh**
**11% imports
Electricity Generation 2023*
*source: https://www.iea.org/
PV capacity (GW)
13.4
5.5
2023
2024
7
2030
Installed Capacity: 24.1 GW

## Slide 6: Electricity Demand – Generation Balance
Net electricity generation in Greece, week 43, 2024*
230
115
0
Price (Euro/MWh)
Day-ahead price
*source: www.energy-charts.info
Characteristics
Unbalance
Curtailment
Price volatility
Grid Capacity

## Slide 7: Grid stability – inertial response
r
m
F
m
x
Inertia constant [s]
e
Grid frequency
Mechanical Power
Electrical Power
T=torque
Grid frequency is determined
by Inertia H and power unbalance
source: foreverspin

## Slide 8: System inertia constant H
Scenario Distributed Energy: DE 2030 & DE 2040
Chart: 
| GR | IE | UK | DE | CH
 | 0 | 2 | 4 | 6 | 8
Country
Inertia H [s]
Inertia
*source: https://www.entsoe.eu/
Notes: NT: National Trends Scenario
GA: Global Ambitions
DE: Distributed Energy

## Slide 9: Frequency Stability
Containing the effect of a grid disturbance – balance market
50Hz
ROCOF
ROCOF
aFRR
FCR
FFR
0.5
2
30
Time [s]
Inertial
Response
Grid
Market
NEW services
900
0.05

## Slide 10: Role of Grid Forming Battery Systems
Grid Stability Support
Frequency Stability
Voltage
Stability
Resonance
Stability
Rotor-angle
Stability
System
Restoration
Wideband oscillation
suppression
Islanding capability
Black start
Virtual Inertial response
0.1 - 100Hz
Grid Forming BESS
5msec
Fast Frequency response
0.5 sec
3 times 10s,10ms
Reactive current
HVRT in low SCR conditions
Maintain synchronism
Restore after faults (transient stability)
130% overvoltage
In several minutes

## Slide 11: Adoption in ancillary services markets
Example: stability market design in the UK
Previously TSOs could rely on abundance of synchronous units able to provide the stability services as a by-product of energy. However with the phase out of conventional generation and dominance of RES generation, TSOs need to procure the services from new resource through a competitive market , BESS+GFM is one of them.
To slow down the rate of change of frequency (RoCoF) and allows frequency response to detect and respond to the failure.
To help maintain system voltage during a fault. SCL is regional, and is expected to decline at different rates across the country.
To help manage voltage by providing immediate, real-time adjustments to reactive power, especially in the grid dominated by renewables.

## Slide 12: Adoption of GFM in Regulations and Standards
RfG2.0 will be released in 2024 and implemented in GF27.
RfG2.0: Include ESS, add RoCoF and Grid forming requirements for PPM in all scenarios of inverter systems connected to the grid: Type A, Type D, Type C, and Type D.
2022 | 2023 | 2024 | 2027
drafts | Public consultation | Released | GF Implementation
Type C and D PPMs (Utility)
Limit transient frequency deviation
Provides additional capacity beyond the inherent ESS
POD (Power Oscillation Damping)
Type B PPMs (C&I/small Utility)
Limiting the frequency deviation
Synthetic inertia
Type A PPMs (domestic/C&I)
PPM as Thevenin Voltage Source
Voltage and phase angle stability during accident
Dynamic performance related to voltage control
Continuous and stable operation when PPM current limit is reached
Ability to activate or deactivate Grid forming mode
2024 released Grid forming ancillary service and related technical requirements
Italy：grid forming capability, including reactive power adjustment, voltage support in the case of faults, black start, inertia synthesis, and POD.
PLANTS WITH ELECTROCHEMICAL STORAGE SYSTEMS
General conditions of connection to Ultra High Voltage and High Voltage networks Protection systems regulation and control
Spain：2023 grid code requires GFM capability, including reactive power adjustment, black start, synthetic inertia, and POD.
Public consultation on the power grid code in 2024, and release and implementation in 2026
GFM part of Network Code:
Requirements for Generators (RfG)
Germany：2024 issued Grid forming ancillary service and develop grid codes ahead of Europe
Italy: 2023 grid code requirements
Spain: Subsidized Project Requirements
2024 Feb.，FNN issued《Grid forming and technical requirements for providing instantaneous inertia 》Draft

## Slide 13: Battery Energy Storage Systems
require must more than just an Li-ion cell module…
Energy Storage System
Power electronics technology
Electrochemical technology
Digital: IT/OT/IoT
Component
(IGBT/MOS)
Material
(GaN/SiC)
Energy storage
management
Heat dissipation
management
Control
(Chip/Algorithm),
BMS, EMS, SCADA
Connection
(IoT)
Sensing
(Digital/Visual)
Cell Quality Control &
Test Standard
Grid
Connection

## Slide 14: Summary and conclusions
BESS can turn imbalance effects in energy markets into commercial opportunity: peak shifting and arbitrage
Battery can be combined with PV (Hybrid PV+BESS) to optimize return in solar
There is the opportunity to capture revenue in merchant markets from new ancillary services
Investors in BESS to manage an application stack combining products from energy and capacity markets.
Grid Forming is a necessary technology as to facilitate the transition of the energy system to enable a large share or renewables in the mix.
It allows for Inverter-based systems, including BESS, to take similar grid supporting behavior as the conventional thermal generators
It provides virtual inertia and other grid stability capabilities
Standards and regulations are well under way and is being adopted in the field in various countries